## Sheet1
Transformer Short Circuit Current Calculation
If applying three phase supply for Short Circuit Test
Transformer Power In KVA (KVA) |  | 25000 | Transformer Rated Current at HV in Amps (IP) | 721.69
Transformer HV Side Voltage (VP) |  | 20000 | Transformer Rated Current at LV in Amps (IS) | 2091.86
Transformer LV Side Voltage (VS) |  | 6900 | Transformer Impedance Voltage | 1962
Transformer % Of Impedance |  | 9.81 | Transformer Short Circuit Current In HV Side ISC (HV Side) | 158.17
Applied Three Phase Voltage V(L-L) |  | 430 | Transformer Short Circuit Current In LV Side ISC (LV Side) | 458.46