## Sheet1
Optimizing Power Systems for Large Motor Startup: Transformer Sizing and Voltage Drop Analysis
| Transformer Detail: |  |  | Transformer Detail:
| Transformer Size | 100 | KVA | Transformer Size | 100 | KVA
| Transformer Secondary Voltage:(v2) | 415 | Volt | Transformer Secondary Voltage:(v2) | 415 | Volt
| % Impedance: (z) | 4% |  | % Impedance: (z) | 4%
| Allowable Voltage Drop in System: | 5% |  | Allowable Voltage Drop in System: | 5%
| Motor Detail ( Only One No of Motor): |  |  | Motors Detail ( More Than One No of Motor):
| Motor Size: | 30 | KW | Total KW of Three Phase Motors: | 30 | KW
| Volt (VM): (L-L) | 415 | Volt | Total KW of Single Phase Motors: | 5 | KW
| Power Factor: | 0.8 |  | Volt: (L-L) | 415 | Volt
| Motor KVA | 12 | KVA | Volt: (L-N) | 239.6074 | Volt
| Motor Code: (KVA/HP) |  |  | Power Factor: | 0.8
| InRush Current at Starting:(Enter If you know otherwise leave it blank) |  |  | Locked Rotor Current: (Max) | 450%
| Enter Motor Full Load Current(Enter If you know otherwise leave it blank ) |  |  | Total Three Phase Motors Full Load Current | 52.1717 | Amp
| Motor Full Load Current: (ILM) | 52.1717 | Amp | Total Single Phase Motors Full Load Current | 26.0843 | Amp
| Locaked Rotor Current Multiplier: (Min) | 5.7 |  | Total Motors Full Load Current | 78.2561 | Amp
| Locaked Rotor Current Multiplier: (Max) | 6.3 |  | Motor InRush KVA At Starting | 253.1201 | KVA
| Locaked Rotor Current (L1): (Min) | 297.3789 | Amp
| Locaked Rotor Current (L2): (Max) | 328.6819 | Amp
| Motor InRush KVA At Starting: (IRSM) | 236.25 | KVA
| How many times Motor Starts per Hours | 2
| Calculations |  |  | Calculations
| Full Load Current of Transformer : (ILX) | 139.1246 | Amp | Full Load Current of Transformer : (IL) | 139.1246 | Amp
| Short Circuit Current at Transformer Secondary: (Isc) | 3478.1157 | Amp | Short Circuit Current at Transformer Secondary: (ISC) | 3478.1157 | Amp
| Max KVA of Transformer at Isc: Q1 | 2500 | KVA | Max KVA of Transformer at Isc | 2500 | KVA
| Motor InRush KVA At Starting:(IRSM) | 236.25 | KVA | Motor InRush KVA At Starting | 253.1201 | KVA
| Voltage Drop at Transformer Secondary Due to Motor inRush: (VD) | 9.45% | 90.55% | Voltage Drop at Transformer Secondary Due to Motor InRush | 10.12% | 89.88%
| Transformer Secondary Voltage | 375.7825 | Volt | Transformer Secondary Voltage | 372.9821 | Volt
| Result |  |  | Result
| (1) Motor Full Load Current <= 65% Transformer Full Load Current | Yes |  | (1) Motor Full Load Current <= 65% Transformer Full Load Current | Yes
| (2) Voltage Drop at Transformer Secondary Due to Motor inRush | High |  | (2) Voltage Drop at Transformer Secondary Due to Motor inRush | High
| (3) Transformer Size:(20% Added due to motor starts more than once/Hour) | 120 | KVA | (3) Transformer Size: | 100 | KVA
| Increase Size of Transformer |  |  | Increase Size of Transformer
Calculation Formulas:
ILX=KVA/(1.732 xV2)
ILM=(KW x 1000)/(1.732 x VM x P.F)
Isc=ILX/z
Q1=(v2 x ISC x ILM x 1.732)/1000
IRSM=(VM x L2 x 1.732)/1000
VD=IRSM/Q1
Code Letter (KVA per HP) -Locked Rotor Current
| Motor Code | Min | Max
1 | A | 3.15
2 | B | 3.16 | 3.55
3 | C | 3.56 | 4
4 | D | 4.1 | 4.5
5 | E | 4.6 | 5
6 | F | 5.1 | 5.6
7 | G | 5.7 | 6.3
8 | H | 6.4 | 7.1
9 | J | 7.2 | 8
10 | K | 8.1 | 9
11 | L | 9.1 | 10
12 | M | 10.1 | 11.2
13 | N | 11.3 | 12.5
14 | P | 12.6 | 14
15 | R | 14.1 | 16
16 | S | 16.1 | 18
17 | T | 18.1 | 20
18 | U | 20.1 | 22.4
19 | V | 22.5
7
5.7
6.3
Note on E28: If motor is to be started more than once per hour add 20% additional KVA