## Cover Page
ELECTRICAL DATASHEET FOR LOW VOLTAGE (LV) SWITCHGEAR
Date | Revision | Datasheet Description | Prepared By | Checked By | Approved By

## LVSWG
Technical Data Sheet - Switchgear
Metal Enclosed Bus - Metric Units
Facility Name: | [8 empty] | Purchase Order No.:
Location: | [8 empty] | Requisition No.:
Product Name: |  | LVSWG | [6 empty] | Job No.:
1 | General
2 | Location: | Indoor | [5 empty] | Outdoor |  |  | Partially Covered
3 |  | Corrosive Agents: | [8 empty] | Coastal or Offshore
4 |  | Pressurized Building | [5 empty] | HVAC Building |  |  | Ventilated Building
5 |  | Earthquake Seismic Zone: | [5 empty] | Other:
6 | Ambient Conditions: | Temperature ('C) |  |  |  |  | Min:22 |  |  |  | Max:40
7 |  | Relative Humidity |  |  |  |  | Min: |  |  |  | Max:
8 |  | Altitude (mm above mean sea level):
9 | Standards
10 |  | UL Listed |  |  | FM |  |  | NEMA | [5 empty] | IEC |  | Other:
11 |  | Unit |  |  | Assembly |  |  | Components
12 | Incoming Power Description
13 | Nominal System: | Voltage (V):415 |  |  |  |  | Frequency (Hz):50 |  |  |  | Other:
14 | Power: |  | Phase:3 |  |  |  | Wire:4 |  |  |  | Other:
15 |  |  | Ungrounded |  |  |  | Grounded |  |  | Grounding Method:Solidly Grounded
16 |  |  | Available Fault Current (kA RMS Sym)*: | [6 empty] | Ground Fault Current (A RMS Sym):
17 | Enclosure
18 | Enclosure: | NEMA 1 |  |  | NEMA 1 w/Gasket |  |  |  | NEMA 12 |  |  | NEMA 3R |  |  | NEMA 4X
19 |  | Ventilated |  |  | Non-Ventilated
20 | Space Heaters: | Rated Voltage: |  |  | 240V |  |  |  | Operating Voltage: |  |  |  | 120V
21 |  |  |  |  | Other | [7 empty] | Other
22 |  | Maximum Heater Surface Temperature:
23 |  | Wattage* |  |  | Thermostate Bypass Switch | [5 empty] | Ammeter
24 |  | Voltage Indicating LED
25 | Corrosion Protection
26 |  | Manufacturer's Standard |  |  |  |  | Aluminum Enclosure |  |  |  | 316 Stainless Steel Hardware
27 |  | GP 19-01-01 |  |  |  |  | Stainless Steel
28 | Control Voltage : |  |  | AC |  | DC | 24Volts |  |  |  | 110Volts |  |  | 120Volts |  | 240Volts
29 | Bus
30 | Materials: |  | Aluminum |  |  |  |  | Copper |  |  | Insulated
31 | Plating*: |  | Tin |  |  |  |  | Silver |  |  | Joints Only
32 | Bracing Amperes RMS Sym*: |  | 22000 |  |  |  |  | 42000 |  |  | 50000 |  |  | 65000 |  | *
33 |  |  | 85000 |  |  |  |  | 100000 |  |  | 200000
34 | Min.Main Bus Rating (Amperes): |  | 600 |  |  | 800 |  | 1200 |  |  | 1600 |  |  | 2000
35 |  |  | 2500 |  |  | 3500 |  | 4000 |  |  | 5000
36 | Insulation: | Type:* | [5 empty] | BIL Rating (kV):* | [5 empty] | Temp Limit (°C):
37 | Neutral Bus: |  | None |  |  | 100% of Main |  | 50% of Main |  |  | Insulated
38 | Ground Bus: |  | None |  |  | 6.4 mm x 25.4 mm |  | 6.4 mm x 50.8 mm |  |  | Unplated Copper. |  |  | Tin-Plated Copper
39 | Incoming Power Section | Close-Coupled to Transformer
40 |  | Close-Coupled to Switchgear | [7 empty] | Open-Air Terminal Bushings
41 |  | Indoor | [6 empty] | Outdoor
42 |  | Enclosed terminal Box | [7 empty] | Open-Air Terminal Bushings
43 |  | Busbar Arrangement
44 |  | Bolted Flange | [6 empty] | With Gasket |  |  |  | With Bolts
45 | Incoming Bus Terminals | Bolts and Flexible Link Connectors (Coordinated to Load Buses)
46 |  | Solid Bus Links | [6 empty] | Insulated Boots
47 |  | Lugs for Cable | [6 empty] | Size |  |  |  | No./Phase:4
48 |  | Connection Bolt-Torque (Nm)* | [8 empty] | Compression Lugs
49 | Loadside Bus Terminals | Bolts and Flexible Link Connectors (Coordinated to Incoming Buses)
50 |  | Solid Bus Links | [6 empty] | Insulated Boots
51 |  | Lugs for Cable | [6 empty] | Size*: |  |  |  | No./Phase:4
52 |  | Connection Bolt-Torque (Nm)* | [8 empty] | Compression Lugs*
53 | Loadside End Section | Close-Coupled | [6 empty] | Terminal Box |  |  |  | Match Load-Side Cubicle
54 |  | Indoors | [6 empty] | Outdoor
55 |  | Bolted Flange | [6 empty] | With Gasket |  |  |  | With Bolts
56 | Supports: | Manufacturer Standard | [6 empty] | Reinforced Polyester |  |  |  | Drawing Included
57 |  | Porcelain
58 |  | Intermediate Support Provision | [6 empty] | Flanged Ends |  |  |  | Other:
59 | Nameplates*
60 | Manufacturer:* |  | Stamped Aluminum | [5 empty] | Stainless Steel |  |  |  | Phenolic
61 |  | Purchase No.: | [6 empty] | OANDO Order No.: |  |  |  | Equipment No.:
62 |  | Year Manufactured: | [6 empty] | Bus Rating: |  |  |  | Min. Letter Height:
63 |  | Rated Voltage (V): | [6 empty] | Short Circuit Rating: KA for secs
64 |  | Busbar Arrangement: | [13 empty] | D
65 | Dimension:* | Overall |  |  |  |  | mm (LXWXH) |  | Panel weight |  | Overall |  |  |  | Kg
66 |  | Incomer |  |  |  |  | mm (LXWXH) |  |  |  | Incomer |  |  |  | Kg
67 |  | Bus Section |  |  |  |  | mm (LXWXH) |  |  |  | Bus Section |  |  |  | Kg
68 |  | Outgoing Tier |  |  |  |  | mm (LXWXH) |  |  |  | Outgoing Tier |  |  |  | Kg
69 | Device: | Three-ply-Phenolic-Background Color: | [6 empty] | Letter Color: |  |  |  | Min. Size:
70 | Other: | Three-ply-Phenolic-Background Color: | [6 empty] | Letter Color: |  |  |  | Min. Size:
71 | Shipping*
72 |  | Crates |  |  | Overseas Shipment |  |  |  | Waterproof |  |  |  | Pallet
73 | Reference Drawings
74 | One-Line | [7 empty] | Dwg No.:
75 |  |  |  | Dwg No.: |  |  |  |  | Dwg No.:
76 | Plans & Elevation: |  |  | Dwg No.: |  |  |  |  | Dwg No.:
77 |  |  |  | Dwg No.: |  |  |  |  | Dwg No.:
Notes

## Incoming Devices-Data
Technical Data Sheet - Switchgear
Metal Enclosed Bus - Metric Units
Facility Name: | [5 empty] | Purchase Order No.:
Location: | [5 empty] | Requisition No.:
Product Name: |  |  | LVSWG |  |  | Project No.:
DATA SHEET FOR LOW VOLTAGE SWITCHGEARS
TECHNICAL DATA FOR INCOMING DEVICES
1 | GENERAL
| TYPE OF BREAKING DEVICE | [5 empty] | Circuit Breaker
| SWITCHING MEDIUM | [5 empty] | Air
| MANUFACTURERS TYPE No. | [10 empty] | **
| TYPE OF DATA GIVEN | [5 empty] | Typical/Design/Tested |  |  |  |  | **
| CONTINUOUS RATED VOLTAGE | [6 empty] | V |  |  |  | **
| IMPULSE TEST VOLTAGE | [6 empty] | V |  |  |  | **
| CONTINUOUS RATED CURRENT | [6 empty] | A @ |  | 0C |  | **
| PEAK ASYMMETRICAL MAKE CURRENT | [6 empty] | kA peak @ 1st half cycle |  |  |  | **
| SYMMETRICAL BREAKING CURRENT | [6 empty] | kA RMS |  | Sec |  | **
| MECHANISM OPENING TIME | [6 empty] | mSec |  |  |  | **
| NO OF POLES | [6 empty] | 4
| TYPE OF MOUNTING | [5 empty] | Withdrawable
| TYPE OF MECHANISM | [5 empty] | Automatic (or) Manual mechanism only
| No. OF AUXILIARY SWITCHES | [5 empty] | 4NO 4NC | above those switches required for control & indication
| UTILISATION CATEGORY | [5 empty] | Category A |  | to IEC 60947-2
| MAIN ISOLATING ARRGTS | [5 empty] | Automatic shutters/padlockable
2 | CIRCUIT BREAKER RATINGS:
| TRANSFORMER INCOMER |  |  |  |  | 2000A, (1No)
| MAIN GENERATOR 1 INCOMER |  |  |  |  | 2000A, (1No)
| MAIN GENERATOR 2 INCOMER |  |  |  |  | 2000A, (1No)
| EMERG. GENERATOR INCOMER |  |  |  |  | 1200A, (1No)
3 | CONTROL SUPPLIES:
| TRIPPING | [5 empty] | 110 | V ac
| CLOSING | [5 empty] | 110 | V ac
| INDICATION | [5 empty] | 110 | V ac
| CHARGING | [5 empty] | 110 | V ac
[7 empty] | 230 | V ac |  | A for | sec | **
4 | MAXIMUM SUPPLY CABLE: CNC-OAO-EL-GEN-SLD-001
Refer Single Line Diagram
5 | GLAND PLATES
Removable/un-drilled (non-magnetic for single core cables)
METERING:
VOLTAGE TRANSFORMER
| CURRENT TRANSFORMER |  |  |  |  | 400/110Vac
i) Transformer Feeder:
[5 empty] | ii) Main Gen. Feeders: | 2000/5A
[5 empty] | iii) Emerg, Gen. Feeder: | 2000/5A
1200/5A
TYPE OF METER:
DIGITAL POWER METER
7 | OPERATIONS
Close/Neutral/Trip (operative in test or isolated position)
8 | INDICATIONS
Open/Closed/tripped/Bus-tie
9 | FAULT PROTECTION
Voltage, Current and Short circuit
10 | INTERLOCKING
i) Bus-tie Breaker / Emerg Gen.Breaker:
Electrical Interlock
11 | One-Line
|  | Dwg No.: |  |  |  | Dwg No.:
12 | Plans & Elevation: | Dwg No.: |  |  |  | Dwg No.:
|  | Dwg No.: |  |  |  | Dwg No.:
Dwg No.:
Notes

## Motor Control Center- Data
Technical Data Sheet -Low Voltage Switchgears
Metal Enclosed Bus - Metric Units
Facility Name: |  |  | BOOSTER PUMP |  |  | Purchase Order No.:
Location: | [5 empty] | Requisition No.:
Product Name: |  |  |  | MCC |  | Job No.:
DATA SHEET FOR LOW VOLTAGE SWITCHGEARS
TECHNICAL DATA FOR MCC SWITCHGEAR
1 |  | TECHNICAL DATA FOR MOTOR CONTROL CENTER (MCC)
2
3 | SOFT START*
4 |  |  |  |  | MANUFACTURER/RANGE * |  | *
5 |  |  |  |  | TYPE OF SOFT START |  | In Line
6 |  |  |  |  | RATED INSULATION VOLTAGE, Ui |  | 690 V
7 |  |  |  |  | RATED OPERATIONAL VOLTAGE, Ue |  | 208 ... 690 V +10 %/-15 %
8 |  |  |  |  | FREQUENCY |  | 50/60 Hz ±5 %
9 |  |  |  |  | STARTING CAPACITY |  | at max rated current Ir: 3 x Ir for 15 sec.
10 |  |  |  |  | OVERLOAD CAPABILITY |  | Overload Class 10
11 |  |  |  |  | AMBIENT TEMPERATURE |  | (i) During operation ±0 … +50 °C (ii) During storage -25… +70 °C
12 |  |  |  |  | ALTITUDE |  | Maximum altitude 4000 m
13 |  |  |  |  | DEGREE OF PROTECTION |  | (i) Main circuit IP10 (ii) Supply and Control circuit IP20
14 |  |  |  |  | SUPPLY CIRCUIT |  | Supply voltage US – one range 100 ... 250 Vac, +10 %/-15 %, (ii) Supply and Control circuit IP20
15 |  |  |  |  | POWER CONSUMPTION |  | * VA
16 |  |  |  |  | TYPE OF MOUNTING |  | Vertical
17 |  |  |  |  | SIGNAL RELAY / AUXILLIARY CONTACTS |  | i) Rated operational voltage Ue 250 V, (ii) Rated thermal current Ith 5 A
18 | [6 empty] | ii) Rated thermal current Ith 5 A
19 | [6 empty] | iii) Rated operational current Ie at AC-15 (Ue = 250 V) 1.5 A
20 |  |  |  |  | PROTECTIONS |  | (i) Electronic overload (ii) Underload protection (iii) Locked rotor protection
21 | [6 empty] | (iv)Phase imbalance (v) Phase reversal protection (vi) High current (8 x Ie)
22 | [6 empty] | (i) Power on – Green (ii) Fault - Red (iii) Protection - Yellow
23 |  |  |  |  | FIELD BUS CONNECTION |  | Connection for Field Bus Plug
24 |  |  |  |  | PTC INPUT |  | i) Switch off resistance 2825 ohm + 20%
25 | [6 empty] | ii) Switch on resistance 1200 ohm + 20%
26 | CONTACTOR:
27 |  |  |  |  | MANUFACTURER/RANGE |  | *
28 |  |  |  |  | RATED VOLTAGE |  | 690 V
29 |  |  |  |  | OPERATING TEMPERATURE RANGE |  |  |  |  | to | degrees C |  |  | *
30 |  |  |  |  | MECHANICAL DUTY CLASS |  |  | Uninterrupted & Class 12 to IEC 60947-4-1
31 |  |  |  |  | UTILISATION CATEGORY |  |  | AC3 to IEC 60947-4-1
32 |  |  |  |  | CO-ORDINATION |  |  | Type 2 to IEC 60947-4-1
33 |  |  |  |  | TYPE OF MOUNTING |  |  | Fixed
34 |  |  |  |  | TYPE OF MECHANISM |  |  | Electrically held in
35 |  |  |  |  | No. OF AUXILIARY CONTACTS |  |  | 2 | N/O | N/O |  | 2 | N/C
36 |  |  |  |  | CONTROL SUPPLY |  | 100 ... 250 Vac, +10 %/-15 %, (ii) Supply and Control circuit IP20
37
38 | MAIN ISOLATOR/FUSES/MCCB/ISOLATOR: | [5 empty] | *
39
40 | GLAND PLATES / ENTRY | [6 empty] | Removeable/undrilled
41
42 | INDICATION LIGHTS | [6 empty] | i) Red - ON (ii) Green - OFF
43
44 | CONTROLS | [6 empty] | Start/Stop pushbutton (Spring return type)
45
46 | EARTH FAULT PROTECTION | [6 empty] | Required on 30kW and above
47
48 | MCUs (Motor Control Units)
49 |  | EACH STARTER TO BE FITTED WITH MOTOR CONTROL UNITS (MCU's) FOR PROTECTION, MONITORING & CONTROL.
50 |  | A HUMAN MACHINE INTERFACE SHALL BE PROVIDED FOR EACH SWITCHBOARD
51
52 |  | EACH MCU SHALL HAVE THE FOLLOWING FEATURES AS A MINIMUM
53 | (a) START/STOP (b) PHASE CURRENTS (c) OVERLOAD PROTECTION (d) EARTH FAULT (e) PHASE FAILURE (f) STALL PROTECTION (g) START LIMITATION
54
55 | ALL MOTOR STARTERS TO INCORPORATE CONTROL FOR MOTOR ANTI-CONDENSATION HEATERS (230V) TO INCLUDE FUSE, CONTROL
56 |  |  | SWITCH, WARNING LIGHT, AUTOMATIC CONTROL VIA CONTACTOR AUXILIARY CONTACT ETC.)
57
58 | [5 empty] | Dwg No.:
59 | [5 empty] | Dwg No.:
60 | [5 empty] | Dwg No.:
61 | [5 empty] | Dwg No.:
Notes

## MCC-1
Technical Data Sheet -Low Voltage Switchgears
Metal Enclosed Bus - Metric Units
Facility Name: |  |  | BOOSTER |  |  | Purchase Order No.:
Location: | [5 empty] | Requisition No.:
Product Name: |  |  |  | MCC 1 |  | Job No.:
DATA SHEET FOR LOW VOLTAGE SWITCHGEARS
TECHNICAL DATA FOR MCC SWITCHGEAR
| Bus | Tag No. |  |  | Description |  | CCT Type | Rating kW | Rating A | Main cable c x mm2 | Remarks
1 | A | Bus A
2 |  | INCOMER |  |  | MCC Incomer Feeder |  | MCCB | 103 | 300 | 4C X 150 | 4 Pole, MCCB
3
4 |  | P-0201 |  |  | Booster PUMP-75KW |  | VFD | 75 | 200 | 3c x 95 | VFD
5
6 |  | P-0202 |  |  | BOOSTER PUMP ( SPARE)-75KW |  | VFD | 75 | 200 | 3c x95 | VFD
Notes
`