## Transformer Protection (IDMT)
Transformer Protection with IDMT Relays (Over Current / Earth Fault / Differential)
Transformer Details |  |  | IDMT Over Current Relay Setting (50/51) |  |  | IDMT Earth Fault Relay Setting (50N/51N) |  |  | Differential Protection Relay
[12 empty] | 3 | 1 | 1 | 1
Transformer Capacity | 13.5 | MVA | LT Side |  |  | LT Side
Primary Voltage (HT) | 132 | KV | Main Protection |  |  | Main Protection
Secondary Voltage(LT) | 27 | KV | Over Load Current : | 125% | X Is | Earth Fault Current : | 20% | X In
Rated Primary Current (Ip) | 102.2727 | Amp | Over Load Current :(In) | 625 | Amp | Earth Fault Current :(Inf) | 125 | Amp | Normal Tap | 100%
Rated Secondary Current (Is) | 500 | Amp | Required Over Current Relay Plug Setting | 1.25 | 1.25 A X In | Required Earth Fault Relay Plug Setting | 0.25 | 0.25 A X In
Max.Earth Fault Current at HV Side (L-G) | 1100 | Amp | Actual Plug Setting of Over Current Relay (I>) | 125% | 1.25 A X In | Actual Plug Setting of Earth Fault Relay (Ie>) | 25% | 0.25 A X In | LT Side
Min.Earth Fault Current at HV Side (L-G) | 1000 | Amp | Pick Up Setting of Over Current Relay (PMS): (I>) | 6.25 | Amp | Pick Up Setting of Earth Fault Relay (PMS): (Ie>) | 1.25 | Amp | Full Load Current | 500 | Amp
Max.Earth Fault Current at LV Side (LG) | 900 | Amp | Fault Current At CT Secondary Side | 45 | Amp | Fault Current At CT Secondary Side | 9 | Amp | Current in Sec. Side of CT | 2.555 | Amp
Min.Earth Fault Current at LV Side (L-G) | 800 | Amp | Plug Setting Multiplier (PSM): | 7.2 | Amp | Plug Setting Multiplier (PSM): | 7.2 | Amp | HT Side
Max.Earth Fault Current at Downstrem of TC (L-G) | 700 | Amp | Curve Selection: | Normal Inverse (NI) |  | Curve Selection: | Normal Inverse (NI) |  | Full Load Current | 102.2727 | Amp
Min.Earth Fault Current at Downstrem of TC (L-G) | 600 | Amp | Time Dial Setting of Over current Relay(TMS): | 0.1 | Sec | Time Dial Setting of Earth Fault Relay(TMS): | 0.1 | Sec | Current in Sec. Side of CT | 2.5568 | Amp
Max.Fault Current at HV Side (L-L) | 5000 | Amp | Time of Operation of Relay | 3.4764 | Sec | Time of Operation of Relay | 3.4764 | Sec | Spil Over current in Relay | 0.0018182 | Amp
Min.Fault Current at HV Side (L-L) | 5500 | Amp | Actual Operaion Time of Relay: (t>) | 0.34764 | Sec | Actual Operaion Time of Relay: (te>) | 0.34764 | Sec | Percentage Differntial Current | 0.071136 | %
Max.Fault Current at LV Side (L-L) | 4500 | Amp | Back Up Protection for Down Stream |  |  | Back Up Protection for Down Stream
Min.Fault Current at LV Side (L-L) | 4000 | Amp | Actual Plug Setting of Over Current Relay (I>>) | 150% | 1.5 A X In | Actual Plug Setting of Earth Fault Relay (Ie>>) | 25% | 0.25 A X In | Highest Tap (+) | 10%
Max.Fault Current at Downstrem Side of TC (L-L) | 3500 | Amp | Pick Up Setting of Over Current Relay (PMS): (I>>) | 7.5 | Amp | Pick Up Setting of Over Current Relay (PMS): (Ie>>) | 1.25 | Amp | Transformation Primary Voltage at + 10% | 145.2 | KV
Min.Fault Current at Downstrem Side of TC (L-L) | 3000 | Amp | Fault Current At CT Secondary Side | 30 | Amp | Fault Current At CT Secondary Side | 6 | Amp | Transformation SecondaryVoltage at + 10% | 27 | KV
CT for O/C & Earth Fault Protection |  |  | Plug Setting Multiplier (PSM): | 4 | Amp | Plug Setting Multiplier (PSM): | 4.8 | Amp | LT Side
CT Ratio (LT Side) |  |  | Curve Selection: | Normal Inverse (NI) |  | Curve Selection: | Normal Inverse (NI) |  | Full Load Current | 500 | Amp
Prim. Current (Amp) | 500 |  | Time Dial Setting of Over current Relay(TMS): | 0.1 | Sec | Time Dial Setting of Earth Fault Relay(TMS): | 0.1 | Sec | Current in Sec. Side of CT | 2.555 | Amp
Sec. Current (Amp) | 5 |  | Time of Operation of Relay | 4.9798 | Sec | Time of Operation of Relay | 4.3929 | Sec | HT Side
CT Ratio (HT Side) |  |  | Actual Operaion Time of Relay: (t>>) | 0.49798 | Sec | Actual Operaion Time of Relay: (te>>) | 0.43929 | Sec | Full Load Current | 92.9752 | Amp
Prim. Current (Amp) | 100 | [7 empty] | Current in Sec. Side of CT | 2.3244 | Amp
Sec. Current (Amp) | 5 |  | Actual Plug Setting of Over Current Relay (I>>>) | 140% | 1.4 A X In | Actual Plug Setting of Earth Fault Relay (Ie>>>) | 25% | 0.25 A X In | Spil Over current in Relay | 0.23062 | Amp
CT for Differential Protection |  |  | Pick Up Setting of Over Current Relay (PMS): (I>>>) | 7 | Amp | Pick Up Setting of Earth Fault Relay (PMS): (Ie>>>) | 1.25 | Amp | Percentage Differntial Current | 9.4528 | %
CT Ratio (LT Side) |  |  | Fault Current At CT Secondary Side | 35 | Amp | Fault Current At CT Secondary Side | 7 | Amp | Highest Tap (-) | 15%
Prim. Current (Amp) | 1000 |  | Plug Setting Multiplier (PSM): | 5 | Amp | Plug Setting Multiplier (PSM): | 5.6 | Amp | Transformation Primary Voltage at - 15% | 112.2 | KV
Sec. Current (Amp) | 5.11 |  | Curve Selection: | Normal Inverse (NI) |  | Curve Selection: | Normal Inverse (NI) |  | Transformation Secondary Voltage at - 15% | 27 | KV
CT Ratio (HT Side) |  |  | Time Dial Setting of Over current Relay(TMS): | 0.1 | Sec | Time Dial Setting of Earth Fault Relay(TMS): | 0.1 | Sec | LT Side
Prim. Current (Amp) | 200 |  | Time of Operation of Relay | 4.2797 | Sec | Time of Operation of Relay | 3.9936 | Sec | Full Load Current | 500 | Amp
Sec. Current (Amp) | 5 |  | Actual Operaion Time of Relay: (t>>>) | 0.42797 | Sec | Actual Operaion Time of Relay: (te>>>) | 0.39936 | Sec | Current in Sec. Side of CT | 2.555 | Amp
HT Side
|  |  | HT Side |  |  | HT Side |  |  | Full Load Current | 120.3209 | Amp
Results of IDMT Relay Settings |  |  | Over Load Current : | 125% | X Ip | Earth Fault Current : | 20% | X In | Current in Sec. Side of CT | 3.008 | Amp
IDMT Over Current Relay Setting |  |  | Over Load Current :(In) | 127.8409 | Amp | Earth Fault Current :(Inf) | 25.5682 | Amp | Spil Over current in Relay | 0.45302 | Amp
LV Side |  |  | Required Over Current Relay Plug Setting | 1.2784 | 1.28 A X In | Required Earth Fault Relay Plug Setting | 0.25568 | 0.26 A X In | Percentage Differntial Current | 16.2869 | %
Plug Setting of Over Current Relay (I>) | 1.25 A X In |  | Actual Plug Setting of Over Current Relay (I>) | 128% | 1.28 A X In | Actual Plug Setting of Earth Fault Relay (Ie>) | 25% | 0.25 A X In
Actual Operaion Time of Relay: (t>) | 0.34764 | Sec | Pick Up Setting of Over Current Relay (PMS): (I>) | 6.4 | Amp | Pick Up Setting of Over Current Relay (PMS): (Ie>) | 1.25 | Amp
Plug Setting of Over Current Relay (I>>) | 1.5 A X In |  | Fault Current At CT Secondary Side | 250 | Amp | Fault Current At CT Secondary Side | 55 | Amp
Actual Operaion Time of Relay: (t>>) | 0.49798 | Sec | Plug Setting Multiplier (PSM): | 39.0625 | Amp | Plug Setting Multiplier (PSM): | 44 | Amp
Plug Setting of Over Current Relay (I>>>) | 1.4 A X In |  | Curve Selection: | Normal Inverse (NI) |  | Curve Selection: | Normal Inverse (NI)
Actual Operaion Time of Relay: (t>>>) | 0.42797 | Sec | Time Dial Setting of Over current Relay(TMS): | 0.1 | Sec | Time Dial Setting of Earth Fault Relay(TMS): | 0.1 | Sec
HV Side |  |  | Time of Operation of Relay | 1.8407 | Sec | Time of Operation of Relay | 1.7807 | Sec
Plug Setting of Over Current Relay (I>) | 1.28 A X In |  | Actual Operaion Time of Relay: (t>) | 0.18407 | Sec | Actual Operaion Time of Relay: (te>) | 0.17807 | Sec
Actual Operaion Time of Relay: (t>) | 0.18407 | Sec | Back Up Protection for Down Stream |  |  | Back Up Protection for Down Stream
Plug Setting of Over Current Relay (I>>) | 1.6 A X In |  | Actual Plug Setting of Over Current Relay (I>>) | 160% | 1.6 A X In | Actual Plug Setting of Earth Fault Relay (Ie>>>) | 25% | 0.25 A X In
Actual Operaion Time of Relay: (t>>) | 0.21054 | Sec | Pick Up Setting of Over Current Relay (PMS): (I>>) | 8 | Amp | Pick Up Setting of Over Current Relay (PMS): (Ie>>>) | 1.25 | Amp
Plug Setting of Over Current Relay (I>>>) | 1.5 A X In |  | Fault Current At CT Secondary Side | 200 | Amp | Fault Current At CT Secondary Side | 40 | Amp
Actual Operaion Time of Relay: (t>>>) | 0.19889 | Sec | Plug Setting Multiplier (PSM): | 25 | Amp | Plug Setting Multiplier (PSM): | 32 | Amp
IDMT Earth Fault Relay Setting |  |  | Curve Selection: | Normal Inverse (NI) |  | Curve Selection: | Normal Inverse (NI)
LV Side |  |  | Time Dial Setting of Over current Relay(TMS): | 0.1 | Sec | Time Dial Setting of Over current Relay(TMS): | 0.1 | Sec
Earth Fault Relay Plug Setting (Ie>) | 0.25 A X In |  | Time of Operation of Relay | 2.1054 |  | Time of Operation of Relay | 1.9506
Actual Operaion Time of Relay: (te>) | 0.34764 |  | Actual Operaion Time of Relay: (t>>) | 0.21054 | Sec | Actual Operaion Time of Relay: (te>>>) | 0.19506 | Sec
Earth Fault Relay Plug Setting (Ie>>) | 0.25 A X In
Actual Operaion Time of Relay: (te>>) | 0.43929 |  | Actual Plug Setting of Over Current Relay (I>>>) | 150% | 1.5 A X In | Actual Plug Setting of Earth Fault Relay (Ie>>>) | 25% | 0.25 A X In
Earth Fault Relay Plug Setting (Ie>>>) | 0.25 A X In |  | Pick Up Setting of Over Current Relay (PMS): (I>>>) | 7.5 | Amp | Pick Up Setting of Earth Fault Relay (PMS): (Ie>>>>) | 1.25 | Amp
Actual Operaion Time of Relay: (te>>>) | 0.39936 |  | Fault Current At CT Secondary Side | 225 | Amp | Fault Current At CT Secondary Side | 45 | Amp
HV Side |  |  | Plug Setting Multiplier (PSM): | 30 | Amp | Plug Setting Multiplier (PSM): | 36 | Amp
Earth Fault Relay Plug Setting (Ie>) | 0.25 A X In |  | Curve Selection: | Normal Inverse (NI) |  | Curve Selection: | Normal Inverse (NI)
Actual Operaion Time of Relay: (te>) | 0.17807 | Sec | Time Dial Setting of Over current Relay(TMS): | 0.1 | Sec | Time Dial Setting of Earth Fault Relay(TMS): | 0.1 | Sec
Earth Fault Relay Plug Setting (Ie>>) | 0.25 A X In |  | Time of Operation of Relay | 1.9889 | Sec | Time of Operation of Relay | 1.8842 | Sec
Actual Operaion Time of Relay: (te>>) | 0.19506 | Sec | Actual Operaion Time of Relay: (t>>>>) | 0.19889 | Sec | Actual Operaion Time of Relay: (te>>>>) | 0.18842 | Sec
Earth Fault Relay Plug Setting (Ie>>>) | 0.25 A X In
Actual Operaion Time of Relay: (te>>>) | 0.18842 | Sec
Normal Inverse (NI)
Very Inverse (VI)
Exteremely Inverse (EI)
Long Inverse
3500
|  |  |  | 35 | 700
56