## IR Value
Minimum Insulation Resistance (IR) Value
Rotating Machine Minimum IR Value |  |  |  | Cable Minimum IR Value
|  |  |  | Type of Cable |  | Multicore
| Machine Terminal to Terminal Voltage | 0.32 | KV | Type of Insulation Material |  | Varnished
[6 empty] | 30 | mm
| IR (Min) for Machine | 1.32 | MΩ | Diameter of Conductor |  | 25 | mm
|  |  |  | Thickness of Jacket Insulation |  | 12 | mm | 61
|  |  |  | Thickness of Conductor Insulation |  | 6 | mm
|  |  |  | IR Value (Min) for Cable |  | 952.979 | MΩ
Transformer Minimum IR Value |  |  |  | Residential Wiring Minimum IR Value
[10 empty] | 50 Hz | 25 Hz | 2
| Frequency | 60 | Hz | (1) No of Outlet (All Point) |  | 20 |  |  | 1 | 1.5 | 1
| Voltage Rating of winding under Test | 440 | Volt | IR (min) value | Excellent | 2.5 | MΩ |  | 2 | 30 | 20
| Rated Capacity of Winding under Test | 11 | KVA | (2) No of Outlet (All Point) |  | 10 |  |  | 3 | 30 | 20
| Select Type of Transformer |  |  | IR (min) value | Excellent | 5 | MΩ
| Tank Oil Filled T.C | 1 | [7 empty] | 1.5
Without Tank Oil filled T.C
Dry or Compound Fill T.C
| IR (Min) for Transformer | 198.9975 | MΩ
[10 empty] | 1 | Paper | 2640 | 1 Core
[10 empty] | 2 | Varnished | 2460 | Multicore
[10 empty] | 3 | ThermoPlastic-Polyethylene | 50000
[10 empty] | 4 | Composite-Polyethylene | 30000
[10 empty] | 5 | Polyvinyle Chloride (60°C) | 500
[10 empty] | 6 | Polyvinyle Chloride (75°C) | 2000
[11 empty] | 2460 | 61

## IR Graph
Insulation Resistance Value Measurement
Name of Equipment
Rated Voltage of Equipment |  | 230 |  |  | Volt
Recommended Megger Size |  | 100V DC or 250V DC | [5 empty] | 100 | 100V DC or 250V DC
Reference Temperature (°C) |  | 40 | [5 empty] | 200 | 100V DC or 250V DC
[8 empty] | 300 | 100V DC or 250V DC
Date | Measured IR Value (MΩ) | Temperature (°C) | Temperature Correction Factor | IR Value after Temperature Adjustment (MΩ) |  |  |  | 400 | 500V DC or 1000V DC
2023-01-01 | 4 | 56 | 3.0314 | 12.1257 |  | 12.1257 | 2023-01-01 | 500 | 500V DC or 1000V DC
2023-01-02 | 3 | 43 | 1.2311 | 3.6934 |  | 3.6934 | 2023-01-02 | 600 | 500V DC or 1000V DC
2023-01-03 | 2 | 33 | 0.61557 | 1.2311 |  | 1.2311 | 2023-01-03 | 700 | 500V DC or 1000V DC
2023-01-04 | 5 | 21 | 0.26794 | 1.3397 |  | 1.3397 | 2023-01-04 | 800 | 500V DC or 1000V DC
2023-01-05 | 2 | 30 | 0.5 | 1 |  | 1 | 2023-01-05 | 900 | 500V DC or 1000V DC
2023-01-06 | 1 | 45 | 1.4142 | 1.4142 |  | 1.4142 | 2023-01-06 | 1000 | 500V DC or 1000V DC
2023-01-07 | 5 | 20 | 0.25 | 1.25 |  | 1.25 | 2023-01-07 | 1100 | 500V DC or 1000V DC
2023-01-08 | 5 | 20 | 0.25 | 1.25 |  | 1.25 | 2023-01-08 | 1200 | 500V DC or 1000V DC
2023-01-09 |  |  | 0 | 0 |  |  | 2023-01-09 | 1300 | 500V DC or 1000V DC
2023-01-10 |  |  | 0 | 0 |  |  | 2023-01-10 | 1400 | 500V DC or 1000V DC
2023-01-11 |  |  | 0 | 0 |  |  | 2023-01-11 | 1500 | 500V DC or 1000V DC
2023-01-12 |  |  | 0 | 0 |  |  | 2023-01-12 | 1600 | 500V DC or 1000V DC
2023-01-13 |  |  | 0 | 0 |  |  | 2023-01-13 | 1700 | 500V DC or 1000V DC
2023-01-14 |  |  | 0 | 0 |  |  | 2023-01-14 | 1800 | 500V DC or 1000V DC
2023-01-15 |  |  | 0 | 0 |  |  | 2023-01-15 | 1900 | 500V DC or 1000V DC
2023-01-16 |  |  | 0 | 0 |  |  | 2023-01-16 | 2000 | 500V DC or 1000V DC
|  |  | 0 | 0 |  |  |  | 2100 | 500V DC or 1000V DC
|  |  | 0 | 0 |  |  |  | 2200 | 500V DC or 1000V DC
|  |  | 0 | 0 |  |  |  | 2300 | 500V DC or 1000V DC
|  |  | 0 | 0 |  |  |  | 2400 | 500V DC or 1000V DC
|  |  | 0 | 0 |  |  |  | 2500 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 2600 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 2700 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 2800 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 2900 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 3000 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 3100 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 3200 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 3300 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 3400 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 3500 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 3600 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 3700 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 3800 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 3900 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 4000 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 4100 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 4200 | 1000V DC or 2500V DC
|  |  | 0 | 0 |  |  |  | 4300 | 1000V DC or 2500V DC
[8 empty] | 4400 | 1000V DC or 2500V DC
[8 empty] | 4500 | 1000V DC or 2500V DC
[8 empty] | 4600 | 1000V DC or 2500V DC
[8 empty] | 4700 | 1000V DC or 2500V DC
[8 empty] | 4800 | 1000V DC or 2500V DC
[8 empty] | 4900 | 1000V DC or 2500V DC
[8 empty] | 5000 | 2500V DC or 5000V DC
[8 empty] | 5100 | 2500V DC or 5000V DC
[8 empty] | 6000 | 2500V DC or 5000V DC
[8 empty] | 7000 | 2500V DC or 5000V DC
[8 empty] | 8000 | 2500V DC or 5000V DC
[8 empty] | 9000 | 2500V DC or 5000V DC
[8 empty] | 10000 | 2500V DC or 5000V DC
[8 empty] | 11000 | 2500V DC or 5000V DC
[8 empty] | 12000 | 2500V DC or 5000V DC
[8 empty] | 13000 | 50000V DC or 10000V DC