## Fault Level Calculator
FAULT LEVEL CALCULATOR
Base MVA |  |  | 10
X'mer Details |  | MVA | % imp |  | % impedance of TF for
X'mer 1 |  | 25 | 10.56 |  | X'mer 1 | 4.224
X'mer 2 |  | 50 | 10.35 |  | X'mer 2 | 2.07
X'mer 3 |  | 50 | 10.28 |  | X'mer 3 | 2.056
fault Level |  | 1 phase | 746
of HV bus |  | 3 phase | 1154
For Single Transformer Parallel |  |  |  |  | For 2 Transformers in Parallel |  |  |  | For 3 Transformers in Parallel
Total parallel impedance |  |  |  | 4.224 | Total parallel impedance |  |  | 1.3892 | Total parallel impedance |  | 4.357
Parameter\phase |  |  | 1 phase | 3 phase | Parameter\Phase |  | 1 phase | 3 phase | Parameter\Phase | 1 phase | 3 phase
Source impedance |  |  | 1.3405 | 0.86655 | Source impedance |  | 1.3405 | 0.86655 | Source impedance | 1.3405 | 0.86655
Total imp. up to LV bus |  |  | 5.5645 | 5.0906 | Total imp. up to LV bus |  | 2.7297 | 2.2558 | Total imp.up to LV bus | 5.6975 | 5.2236
SC MVA |  |  | 179.7112 | 196.4424 | SC MVA |  | 366.3418 | 443.3096 | SC MVA | 175.5159 | 191.4404