## Knee Point Voltage
Knee Point Voltage Calculation for HT Motor
Motor Set capacity | = | 1600 | kW
System Voltage | = | 6.6 | kV
CT Primary | = | 200 | Amps
CT Seconday | = | 1 | Amps
CT ratio | = | 200
Considering 10%,-VE tolerance,Voltage | = | 5940 | Volts
MVA Rating | = | 2 | MVA
Starting current of HT Motor is 7.2 times of normal current rating | = | 1457.998 | A
It is recommended to take the twice of starting current for calcualation because of intial peaks. | = | 2915.996
Fault Current at Secondary side of CT, | = | (Starting Current )/CT ratio
Fault Current at Secondary side of CT, i.e,Ist | = | 2915.996 | Amps
Lead Resistance | = | 7.41 | ohms/Km
Distance between CT and Relay | = | 50 | meters
Number of runs | = | 2
Hence the Lead Resistance, RL | = | ((ohms/Km)*distance*Number of runs)/1000
| = | 0.741 | ohms
Relay Resistance , R relay | = | 1 | ohms
Total Resistance | = | 1.741
CT Secondary Resistance, Rct | = | 1 | ohms
Knee Point Voltage,Vk | = | 2( Ist / CTratio(Rct+RL) )
| = | 79.9275 | Volts
Therefore Selected Knee Point voltage is | >= | 80 | Volts
Primary Operated Current (POC) | = | 30% of Rated current
Relay Setting | = | 10% i.e 0.1
POC | = | ( relay stetting + Imag X Number of CT's ) X CT Ratio
From above formula Imag | = | 86.675 mA
ForumElectrical.com
ForumElectrical.com