## Reactor Switching Voltage Drop
Reactor Switching Voltage Drop Calculator
1 | Base Selection
| Base KV | 400 | kV
| Base MVA | 60 | MVA
| Base Current = Base MVA *1000/ ( 1.732 X Base KV) Amp | 86.6051 | A
| Base Impedance = (Base KV)2 / Base MVA | 2666.6667 | Ω
2 | Reactor Details
| Rating of reactor in MVAr | 50 | MVAr
| Voltage ( KV) | 400 | kV
| Impedance of Reactor | 3200 | Ω
| Voltage in pu | 1 | pu
| Impedance of Reactor in pu | 1.2 | pu
3 | Source Details
| Source Voltage (kV) | 440 | kV
| Fault kA of source (kA) = | 8.1534 | kA
| Fault MVA of source = | 6213.5278 | MVA
| Voltage in pu | 1.1 | pu
| Zsource = Source Impedance | 31.1578 | Ω
| Zsource in pu | 0.011684 | pu
4 | Thevenin voltage
| Thevenin Voltage (VTH) in pu | 1.0894 | pu
| Thevenin Impedance in pu | 0.011572 | pu
| Percentage voltage drop (%) | 0.9643%
| Voltage drop in pu | 0.010607 | pu
| Voltage drop in kV | 4.2429 | kV
| Voltage in kV | 435.7571 | kV
Source Voltage
410 kV
Source Impedance
VTH
Voltage after Reactor
Reactor Impedance